## Calculation
>
Network load calculation tool
|  | Minimum transmit clock |  |  |  | 1 |  |  | ms
Input area
|  |  |  | Remote IO |  |  |  |  | Drives | [8 empty] | Data rate calculation
|  | Device group |  | Group 1 | Group 2 | Group 3 |  |  | Group 4 | Group 5 | Group 6 | [6 empty] | Remote IOs |  |  |  | Drives
|  | Number of devices |  | 1 | 0 |  |  |  | 0 | [5 empty] | Multiplied by the |  | Input | 1184 | 0 | 0 | Bit | 0 | 0 | 0 | Bit
[15 empty] | number of devices |  | Output | 1264 | 0 | 0 | Bit | 0 | 0 | 0 | Bit
Use of IRT
Number of modules
|  | Input |  | 40 | 10 |  |  |  | 1
|  | Output |  | 30 | 10 | [9 empty] | Not multiplied by the |  | Input | 1184 | 704 | 704 | Bit | 1200 | 704 | 704 | Bit
[15 empty] | number of devices |  | Output | 1264 | 704 | 704 | Bit | 1200 | 704 | 704 | Bit
Net data per device
|  | Input data |  | 30 | 20 |  | Bytes |  | 100 |  |  | Bytes
|  | Output data |  | 40 | 20 |  | Bytes |  | 100 |  |  | Bytes
[15 empty] | Multiplied by the |  | Input | 296 | 0 | #DIV/0! | kBit/s | 0 | #DIV/0! | #DIV/0! | kBit/s
|  | Update time per device group | [12 empty] | number of devices |  | Output | 158 | 0 | #DIV/0! | kBit/s | 0 | #DIV/0! | #DIV/0! | kBit/s
|  | Input |  | 4 | 1 |  | ms |  | 1 |  |  | ms
|  | Output |  | 8 | 1 |  | ms |  | 1 |  |  | ms
[15 empty] | Not multiplied by the |  | Input | 296 | 704 | #DIV/0! | kBit/s | 1200 | #DIV/0! | #DIV/0! | kBit/s
[15 empty] | number of devices |  | Output | 158 | 704 | #DIV/0! | kBit/s | 1200 | #DIV/0! | #DIV/0! | kBit/s
Clock factors
|  | SendClock Factor |  | 32 | 32 | 32 |  |  | 32 | 32 | 32 |  | Output area |  | IRT / RT active ? |  |  | FALSE | FALSE | FALSE |  | FALSE | FALSE | FALSE
|  | Reduction Ratio Output |  | 4 | 1 | 0 |  |  | 1 | 0 | 0
|  | Reduction Ratio Input |  | 8 | 1 | 0 |  |  | 1 | 0 | 0
[16 empty] | 0.03125 |  | 0
|  | Network load per device | [13 empty] | 0.0625 |  | 0
|  | Resulting PROFINET network load | Input | 0.296 | 0.704 |  | MBit/s | Input | 1.2 |  |  | MBit/s |  |  |  | 0.125 |  | 0
0.25
|  |  | Output | 0.158 | 0.704 |  | MBit/s | Output | 1.2 |  |  | MBit/s |  |  |  | 0.5
1
|  | Network load per device group | [13 empty] | 2
|  | Resulting PROFINET network load | Input | 0.296 | 0 |  | MBit/s | Input | 0 |  |  | MBit/s |  |  |  | 4
8
|  |  | Output | 0.158 | 0 |  | MBit/s | Output | 0 |  |  | MBit/s |  |  |  | 16
32
64
128
256
|  | Common network load on one | [13 empty] | 512
1024
|  |  | Output | 0.158 |  | MBit/s |  | Input | 0.296 |  | MBit/s |  |  |  |  | 2048
v
Packet size calculation
|  |  |  | Remote IOs |  |  |  |  | Drives
| Packet size before checking |  | Input | 100 | 40 | 0 |  |  | 102 | 0 | 0
|  |  | Output | 110 | 40 | 0 |  |  | 102 | 0 | 0
| Packet size after checking |  | Input | 100 | 40 | 40 |  |  | 102 | 40 | 40
|  |  | Output | 110 | 40 | 40 |  |  | 102 | 40 | 40
| Header + Interframe space + Preamble |  | IRT / RT | 48 | 48 | 48 |  |  | 48 | 48 | 48
| Overall packet size |  | Sum in | 148 | 88 | 88 |  |  | 150 | 88 | 88
|  |  | Sum out | 158 | 88 | 88 |  |  | 150 | 88 | 88
| Check of the maximum packet size |  | without IRT | 0 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | with IRT | 0 | 0 | 0 |  |  | 0 | 0 | 0
Note on C13: Determination of 6 debice group, where 3 of them are dedicated to one device type.
Note on C15: Input of the number of devices per device group.
Note on C17: Definition if IRT is used or not.
Note on C19: Input of the numbers of modules depending of the transmission direction.
Note on C24: Input of the summarized net data depending of the transmission direction.
Note on C29: Input of the update time of a PROFINET device depending of the transmission direction (Dropdown or manuel)
Note on C35: Display of the clock factors of the PROFINET transmission system.
Note on C42: Value of the network load generated by one PROFINET device of this device group, depending of the the transmission direction.
Note on C47: Network load generated by the common device group, depending of the transmission direction.
Note on C55: Summarized network load of all device groups, seperated by the direction of transmission.
Note on E12: Input area for peripheral devices with a different number of modules and data amount for each transmission direction (e.g. Remote IOs).
Note on L9: Selection of the minimum transmission clock via dropdown menue
Note on L12: Input area for PROFINET devices with an identical number of modules for input and output transmission direction, but different data amount per direction (e.g. drives).

## User manual
User manual

## Program flowchart
Programm flowchart